TYPICAL SPECIFICATION

HYPO TRAK Digital Display

SPECIFICATION SECTION 11245 - Chemical Feeder Accessories

SPECIFICATION SECTION 11240 - Chemical Metering Pump Accessories

The remote mounted LCD indicator shall carry CE marking and shall be housed in a NEMA 4X, UL approved enclosure. All operations shall be keypad operated & menu driven in order to avoid compromising the NEMA 4X seal at anytime.  The alphanumeric LCD readout shall have backlighting for readability in low light conditions.  Power requirement shall be ______________      ( 110 VAC, 220 VAC or 24 VDC)

Numerical display shall have 6 full active digits and adjustable bar graph to display remaining hypo in Lbs or gallons.  In addition, indicator shall display hypochlorite concentration, hypo feed rate, age of hypo in days and equivalent Lbs of pure chlorine gas.  3 user programmable degradation curves shall be available for various temperature conditions and/or hypochlorite characteristics.  Indicator shall output net inventory via a 4-20mA signal for remote monitoring.   Indicator shall display and have relay contacts available for the following alarm conditions: High Chlorate Warning, Vapor Locked Pump, Low Level and High Level.

Digital display shall carry a Full Five (5) Year Factory Warranty.  “Limited” Warranties shall be considered unacceptable.   Full scale accuracy shall be better than 1/4 of 1%.  Digital display shall be HYPO TRAK Sodium Hypochlorite monitoring system Model HT1 as manufactured by FORCE FLOW, 2430 Stanwell Drive, Concord, CA 94520 USA (www.forceflow.com).