TYPICAL SPECIFICATION

SOLO® G2

150 LB. CYLINDER SCALE

SPECIFICATION SECTION 11261 - Chlorination Equipment

A quantity of ____chlorine/S02 scales shall be provided and shall be of the digital readout/electronic load cell type.   Scale platform shall be constructed of non-corrosive PVC plastic and sized to accept 150 lb. cylinders from 10 1/4" (260mm) to 10 1/2" (267mm) in diameter.   Platform height shall be no more than 1-5/8" (38mm) to allow easy handling and unloading of cylinders.    Platform scale coating system shall be a minimum dry thickness of 80 mils and be resistant to moisture, chemicals, abrasion, impact and UV light.

Scale shall be of the single load cell design.  Weight shall be transferred via a pivoted platform to a single stainless steel canister load cell of the electronic strain gauge type.  Load cell shall be mechanically sealed with o-rings.  Potted-type load cells shall not be accepted.  Flexible cable shall connect load cell to indicator to allow easy remote installation of the readout.  Cable length shall be _____ feet (10'/3M standard).    Cylinder chaining bracket shall be wall mounted and use a double coil chain and a spring loaded snap hook to sure cylinder.  Chaining bracket shall have an integral tool rack for storing cylinder change-out tools.

Indicator shall monitor__________(1 or 2 ) channels. The remote mounted LCD indicator shall carry CE marking and shall be housed in a NEMA 4X, UL approved enclosure. All operations shall be keypad operated & menu driven in order to avoid compromising the NEMA 4X seal at anytime.  The alphanumeric LCD readout shall have backlighting for readability in low light conditions.  Power requirement shall be ______________( 110 VAC, 220 VAC or 24 VDC)

A 6 digit numerical display shall give operator the ability to monitor chemical by weight (lb or kg) or volume (gallons or liters).  A bar graph display shall read 0-100% for the net contents.  A dual mode TARE key shall allow user to enter the tare weight of the vessel or enter the net weight of the chemical depending on application needs. A diagnostics menu shall allow recalibration without the need to apply field test weights.  A user adjustable filter function shall stabilize display in the event of vibration from pumps or mixers in the immediate vicinity of the scale.

Indicator shall output net weight via a 4-20mA signal and full scale output shall be user adjustable via the keypad.  Indicator shall have four adjustable set points to display low or high level conditions on the indicator.

OPTIONAL:    Set points shall activate ______ (up to four) ½ Amp dry contact relays.

Scale shall carry a Full Five (5) Year Factory Warranty.  “Limited” Warranties shall be considered unacceptable.   Full scale accuracy shall be better than 1%.   Scale shall be CHLOR-SCALE 150® with TUF-COATTM coating and SOLO® G2 digital display, Model GR150-____  manufactured by FORCE FLOW, 2430 Stanwell Drive, Concord, CA 94520 USA  (www.forceflow.com).

SCALE WITH INDICATOR:

No. of Cylinders		Model		Metric Model	No. of Channels

1-Cylinder		GR150-1   	GR100K-1	1-Channel Solo G2

2-Cylinder		GR150-2   	GR100K-2	2-Channel Solo G2

FORCE FLOW   1-800-893-6723

FAX: 925-686-6713    www.forceflow.com    info@forceflow.com

CYL/SOLOG2

02/26/09