TYPICAL SPECIFICATION

WIZARD® 4000

150 LB. CYLINDER SCALE

SPECIFICATION SECTION 11261 - Chlorination Equipment

SCALE PLATFORM:   A quantity of ____ chlorine/SO2 cylinders shall be weighed.  Chlorine/ SO2 Cylinder scales shall be of the digital readout/strain gage load cell type.   Each scale platform shall be constructed of non-corrosive PVC plastic and sized to accept one (1) 150 lb cylinder from 10 ¼” – 10 ½” (260mm – 267mm). Platform scale coating system shall be a minimum dry thickness of 80 mils and be resistant to moisture, chemicals, abrasion, impact and UV light. Load cell cable length shall be a minimum of 10 feet.  A wall mounted cylinder restraining bracket with integral tool rack shall be provided.

INSTRUMENT ENCLOSURE, OUTPUTS & ALARMS:  Indicator shall carry CE marking and shall be housed in a NEMA 4X, UL approved enclosure.   Indicator shall have a 20 key digital keypad & ability to display 2 scales at a time on a backlit alphanumeric display.  If more than 2 scales are being monitored, display shall automatically scan all scales in the system.   Indicator shall have adjustable 4-20mA signals that output net weight and chemical feed rate for each scale.  Indicator shall display an alarm in any of the following conditions: Low level, high level, low feed rate, high feed rate, max daily use, min daily use, supply exhausted and load cell failure.  An alarm log shall store the most recent 10 alarm conditions with time and date of occurrence.  A quantity of  ____ relays (up to 12 per indicator) shall be provided for remote alarm indication or transfer pump control.   Indicator shall be enabled with MODBUS protocol for remote RS-485 serial communications.

DISPLAY & INVENTORY CONTROL SOFTWARE:  Keypad and Menu items shall have independent password protection to prevent unauthorized operation.  Both a numerical and a bar graph display shall give operator the ability to monitor chemical by weight, volume or percent full.    Each channel shall have a user selectable, two digit scale ID number and shall display net remaining, pure chemical remaining, feed rate, daily usage, total amount used, days until empty, gross weight and tare weight.    A TANK LOAD key shall pause & project usage accumulation during chemical re-supply to maintain accurate usage data over multiple tank loads.  A data log shall store the DAILY USAGE for each of the previous 31 days.  Indicator re-calibration in the field shall be accomplished through the keypad and shall not require the use of dead weights.

Scale shall carry a Full Five (5) Year Factory Warranty.  “Limited” warranties shall be considered unacceptable.   Full scale accuracy shall be better than 1%.   Scale shall be CHLOR-SCALE® 150 with TUF-COATTM Environmental Armor and WIZARD 4000® digital display, Model WR______-___, as manufactured by FORCE FLOW, 2430 Stanwell Drive, Concord, CA 94520 USA (www.forceflow.com).

Model Numbers:

PLATFORM & INDICATOR:

No. of Cylinders		Models		Metric Modes		No. of Channels

1-Cylinders 		WR150-1		WR100K-1		1-Channel Wizard

2-Cylinders 		WR150-2		WR100K-2		2-Channel Wizard

3-Cylinders 		WR150-3		WR100K-3		3-Channel Wizard

4-Cylinders 		WR150-4		WR100K-4		4-Channel Wizard

File:   _WEB\SPECS\SPC150WZ

FORCE FLOW  1-800-893-6723

FAX: 925-686-6713

CYL/WIZ

09/03/03