TYPICAL SPECIFICATION

SOLO® G2

CHEMICAL DAY TANK SCALES

SPECIFICATION SECTION 11245 - Chemical Feeders

SPECIFICATION SECTION 11240 - Chemical Metering Pumps

A quantity of ____chemical scales of ___________ lbs. (kgs.) capacity shall be provided and shall be of the digital readout/electronic load cell type.  Scale platform shall be sized to accept a ____inch diameter tank.   Four (4) adjustable hold down lugs shall be provided on the platform to increase lateral stability and to allow the use of hold down straps for securing the vessel to the platform.   Platform scale coating system shall be a minimum dry thickness of 80 mils and be resistant to moisture, chemicals, abrasion, impact and UV light.

Scale shall be of the single load cell design.  Weight shall be transferred via a pivoted platform to a single, NTEP approved load cell of the shear beam strain gauge type.  Flexible cable shall connect load cell to indicator to allow easy remote installation of the readout.  Cable length shall be ____ ft. (meters) (20'/6M standard).

Indicator shall monitor__________(1 or 2 ) channels. The remote mounted LCD indicator shall carry CE marking and shall be housed in a NEMA 4X, UL approved enclosure. All operations shall be keypad operated & menu driven in order to avoid compromising the NEMA 4X seal at anytime.  The alphanumeric LCD readout shall have backlighting for readability in low light conditions.  Power requirement shall be ______________( 110 VAC, 220 VAC or 24 VDC)

A 6 digit numerical display shall give operator the ability to monitor chemical by weight (lb or kg) or volume (gallons or liters).  A bar graph display shall read 0-100% for the net contents.  A dual mode TARE key shall allow user to enter the tare weight of the vessel or enter the net weight of the chemical depending on application needs. A diagnostics menu shall allow recalibration without the need to apply field test weights.  A user adjustable filter function shall stabilize display in the event of vibration from pumps or mixers in the immediate vicinity of the scale.

Indicator shall output net weight via a 4-20mA signal and full scale output shall be user adjustable via the keypad.  Indicator shall have four adjustable set points to display low or high level conditions on the indicator.

OPTIONAL:    Set points shall activate ______ (up to four) ½ Amp dry contact relays.

Scale shall carry a Full Five (5) Year Factory Warranty.  “Limited” Warranties shall be considered unacceptable.  Full scale accuracy shall be better than 1/4 of 1%.   Scale shall be CHEM-SCALETM with TUF-COATTM coating, Model ____-DR_____LP , and SOLO® G2 digital display Model SRG2-____ (1 or 2 channel), as manufactured by FORCE FLOW, 2430 Stanwell Drive, Concord, CA 94520 USA (www.forceflow.com).

Model Numbers:

INDICATOR:	SRG2-1		One Channel

SRG2-2 		Two Channel

PLATFORM:

Capacity	30" x 30"		40" x 40"		50" x 50"		60" x 60"

1,000 lb.	30-DR10LP

2,000 lb.	30-DR20LP	40-DR20LP

3,000 lb.	30-DR30LP	40-DR30LP

4,000 lb.			40-DR40LP

5,000 lb.					50-DR50LP	60-DR50LP

6,000 lb.					50-DR60LPH	60-DR60LPH

8,000 lb.					50-DR80LPH	60-DR80LPH

10,000 lb.							60-DR100LPH

12,000 lb. (Special)						60-DR120LPH

Consult Factory for Stainless Steel or Metric Models

FORCE FLOW   1-800-893-6723

FAX: 925-686-6713    www.forceflow.com    info@forceflow.com