TYPICAL SPECIFICATION

HYDRAULIC CENTURY®

MULTIPLE TANK TON CHLORINE SCALE

SPECIFICATION  SECTION 11261 - Chlorination Equipment

Scales shall be of the hydraulic load cell type.   Scale frame will be epoxy finished and sized to accept _____ (3,   4,   5  or  6) 3,600 lb/1,632 kg. chlorine or SO2 containers.   It shall have required number of heavy duty bushed bearing trunnions installed for each container to allow easy container rotation.   Scale shall be of such a size that it is within the dimensions of the tanks it supports.  Frame shall be constructed of ASTM grade A36 structural steel and shall transfer load via levers to a single hydraulic load cell.  No hydraulic totalizers or summing devices shall be required.

Load cell shall be of the temperature stable, rolling diaphragm type.  Load plate shall be able to tilt to 4 degrees without affecting accuracy.   Flexible tubing shall lead from the cell to allow  remote installation of the dial and shall be ________ ft. (meters) (20'/6M standard) in length.   Load cell system shall require no electric power and shall be immune to all RFI/EFI, power failures and lightening strikes.

Dial diameter shall be 12" inches  and read zero to _________ lbs (kgs) with provision for tare adjustment.  Dial shall be temperature stable with damper installed to prevent shock damage.

Scale shall carry a minimum Five (5) Year Factory Warranty.    “Limited” Warranties shall be considered unacceptable.

Full scale accuracy shall be better than ½ of 1%.    Scale shall be CHLOR-SCALE® with hydraulic CENTURY® dial indicator,  Model 12D______ as manufactured by FORCE FLOW, 2430 Stanwell Drive, Concord, CA 94520 USA (www.forceflow.com),  or equal.

OPTION 1:	Scale shall have a SATELLITE® loop powered 4-20mA output proportional to gross weight.

OPTION 2:	Scale shall have a 5amp low level contact with manual reset button.

Model Numbers:

PLATFORM & INDICATOR:

No. of Ton Container Tanks		Model  (Capacity lbs)	Metric Model  (Capacity kgs)

3-Tank Scale			12D120	 (12,000 lb)	12D60K	  (6000 kg)

4-Tank Scale			12D160	 (16,000 lb)	12D80K	  (8000 kg)

5-Tank Scale 			12D200	 (20,000 lb)	12D100K  (10,000 kg)

6-Tank Scale			12D240	 (24,000 lb)	12D120K  (12,000 kg)

File:   _WEB\SPCS\SPCMULHY   02/03/03

FORCE FLOW   1-800-893-6723

FAX: 925-686-6713

MULT/HYD