TYPICAL SPECIFICATIONS

WIZARD AUTO-REFILL CONTROLLER/INDICATOR

AUTO REFILL CONTROLLER  shall provide both manual and automatic control for chemical transfer pump, valve or feeder to transfer chemical from bulk storage supply to a day tank or hopper.  This control shall be accomplished by monitoring the weight (level) of the day tank/hopper on the scale platform connected to a local weight indicator with an integrated Hand-Off-Auto Switch (HOA Switch).

INDICATOR  shall carry CE marking and shall be housed in a NEMA 4X, UL approved enclosure.  Operator shall be able to monitor chemical by weight, volume or percent full.  Indicator shall display NET REMAINING, FEED RATE, DAILY USAGE, TOTAL AMOUNT USED & DAYS UNTIL EMPTY.   A data log function shall store the DAILY USAGE for each of the previous 31 days.  An integrated Hand-Off-Auto switch shall be provided with spring return from the Hand position.  An adjacent green indicator lamp shall be illuminated when refilling the day tank/hopper.  In order to preserve accurate chemical usage data in the automatic mode, usage accumulator shall automatically “Pause and project” chemical usage during the refilling process.

OUTPUTS  shall include 6 process alarms: low and high level, low and high feed rate, slow refill (bulk supply empty), and max daily use.  4-20mA outputs of the net chemical weight remaining & net chemical feed rate shall also be provided.  The Wizard Indicator/Controller shall provide 3 amps solid state relay outputs for operation of the chemical transfer device and 0.5 amps dry contacts for the chemical process alarms.

PLATFORM SCALE  shall be of the single load cell design.   Platform scale coating system shall be a minimum dry thickness of 80 mils and be resistant to moisture, chemicals, abrasion, impact and UV light.  Weight shall be transferred via lever(s) to a single NTEP approved load cell of the shear beam strain gauge type.  Scale capacity shall be ________ lbs/kgs and cable length shall be ________ ft/M (20 ft standard) in length.  Scale shall carry a Ful Five (5) Year Factory Warranty and shall have an accuracy of better than 1/4 of 1%.  Scale shall be Model No. ___________ with TUF-COAT™ coating and controller/indicator shall be WIZARD©ARC controller Model 4000-ARC, as manufactured by FORCE FLOW, 2430 Stanwell Drive, Concord, CA 94520 USA ( or equal.

Specifications:

Dimensions: 10.5" H x 8.5" W x 6 5/8" D

Power: 110, 220, 240 VAC, 50/60 Hz, 5 watts

Operating Temperature: 32F to 122 F (0-50 C)

Enclosure: NEMA 4X, UL Listed, CE Marked

Inputs:   Up to 8 Strain Gauge load cells

Outputs:  Control relays: 3 amps Solid State    Alarm relays: 0.5 amps Dry contacts.