TYPICAL SPECIFICATION

HYDRAULIC CENTURY®

STATIONARY BULK TANK SCALE

SPECIFICATION  SECTION 11261 -   Chlorination Equipment

Tank scales shall be of the hydraulic cell type.

Load cell shall be of the temperature stable, rolling diaphragm type.   Load plate shall be able to tilt 4 degrees without affecting accuracy to allow easy installation.    Flexible hose shall lead from the load cell to allow easy remote installation of the dial and shall be _____ ft. (meters) in length (20'/6M standard).    Load cell system shall require no electric power and shall be immune to all RFI/EFI, power failures and lightening strikes

Dial diameter shall be 12 inches and read zero to _________ lbs. (kgs) with provision for tare adjustment.   Dial shall be calibrated 2:1 to load cell.   Tare weight of tank will be _______ lbs. (kgs).     Tank, hinge and hold down devices to be furnished by others.

Shall carry a minimum Five (5) Year Factory Warranty.   “Limited” Warranties shall be considered unacceptable.

Full scale accuracy shall be better than ½ of 1%.   Scale shall be CHLOR-SCALE® with hydraulic CENTURY® dial indicator, Model 12D_____ as manufactured by FORCE FLOW, 2430 Stanwell Drive, Concord, CA 94520 USA (www.forceflow.com), or equal.

OPTION 1:	Scale shall have a SATELLITE® loop powered 4-20mA output proportional to gross weight.

OPTION 2:	Scale shall have a 5amp low level contact with manual reset button.

OPTION 3:	Scale shall have a 10amp fixed alarm pressure switch.

Model Numbers:

LOAD CELL SYSTEMS:

Model Number (Capacity lbs)			Metric Model (Capacity kgs)

12D300   (30,000 lbs)			12D150K   (15,000 kilo)

12D400   (40,000 lbs)			12D200K   (20,000 kilo)

12D500   (50,000 lbs)			12D250K   (25,000 kilo)

12D600   (60,000 lbs)			12D300K   (30,000 kilo)

For other capacities and dial sizes, consult factory.    Tank & Saddle by others.

File:   _WEB\SPECS\SPCSTAHY   02/18/03

FORCE FLOW 1-800-893-6723

FAX: 925-686-6713

STATIONARY/HYD