TYPICAL SPECIFICATION

WIZARD® 4000 with

PROCELL® TANK WEIGHING ASSEMBLIES

SPECIFICATION SECTION 11245 - Chemical Feeders,

SPECIFICATION SECTION 11261 - Chlorination Equipment, or

SPECIFICATION SECTION 11240 - Chemical Metering Pumps:

TANK WEIGHING ASSEMBLIES:    A quantity of _____(1, 2, 3, or 4) tank weighing assemblies shall be installed for each tank/hopper/bin. Each tank weighing assembly shall have a capacity of _______ lbs (kgs) for a total system capacity of _______ lbs (kgs).    Each tank weighing assembly shall consist of a nickel plated load cell of the shear beam strain gauge type and appropriate mounting hardware.  Flexible cable shall connect load cell to indicator for easy remote installation of the readout.  Cable length shall be _____ feet, 20' (6M) standard.    Tank weighing assemblies shall be self-checking and have provisions for thermal expansion and contraction.  Tank weighing assembly load plate shall be able to compensate for mounting surfaces up to 4 degrees off-level.

INSTRUMENT ENCLOSURE, OUTPUTS & ALARMS:  Indicator shall carry CE marking and shall be housed in a NEMA 4X, UL approved enclosure.   Indicator shall have a 20 key digital keypad & ability to display 2 scales at a time on a backlit alphanumeric display.  If more than 2 scales are being monitored, display shall automatically scan all scales in the system.   Indicator shall have adjustable 4-20mA signals that output net weight and chemical feed rate for each scale.  Indicator shall display an alarm in any of the following conditions: Low level, high level, low feed rate, high feed rate, max daily use, min daily use, supply exhausted and load cell failure.  An alarm log shall store the most recent 10 alarm conditions with time and date of occurrence.  A quantity of ____ relays (up to 12 per indicator) shall be provided for remote alarm indication or transfer pump control.   Indicator shall be enabled with MODBUS protocol for remote RS-485 serial communications.

DISPLAY & INVENTORY CONTROL SOFTWARE:  Keypad and Menu items shall have independent password protection to prevent unauthorized operation.  Both a numerical and a bar graph display shall give operator the ability to monitor chemical by weight, volume or percent full.    Each channel shall have a user selectable, two digit scale ID number and shall display net remaining, pure chemical remaining, feed rate, daily usage, total amount used, days until empty, gross weight and tare weight.    A TANK LOAD key shall pause & project usage accumulation during chemical re-supply to maintain accurate usage data over multiple tank loads.  A data log shall store the DAILY USAGE for each of the previous 31 days.  Indicator re-calibration in the field shall be accomplished through the keypad and shall not require the use of dead weights.

System shall carry a Full Five (5) Year Factory Warranty.   “Limited” warranties shall be considered unacceptable.   Pivoted weighing systems shall have an accuracy of 1/4 of 1%, all others 1/10 of 1%.       Tank weighing assembly shall be PROCELL® Model PC-______ and digital indicator shall be WIZARD 4000® Model 4000-___, manufactured by FORCE FLOW, 2430 Stanwell Drive, Concord, CA 94520 USA (www.forceflow.com).

PROCELL® TANK WEIGHING ASSEMBLIES:

Model Numbers:		Capacities

PC820			5000 lb. - 10,000 lb.  (227 kg – 4,536 kg)

PC160			1,000 lb. - 75,000 lb.  (454 kg – 34,030 kg)

INDICATOR:

  - 1-Channel Wizard

  - 2-Channel Wizard

  - 3-Channel Wizard

4000-4   4-Channel Wizard

File: _WEB\SPECS\SPCPWRWZ

FORCE FLOW   1-800-893-6723

FAX: 925-686-6713    www.forceflow.com    info@forceflow.com

TWA/WIZ

09/03/03