TYPICAL SPECIFICATION

SOLO® G2

SINGLE or DUAL TANK TON CHLORINE SCALES

SPECIFICATION SECTION 11261 - Chlorination Equipment

A quantity of ______ Chlorine/SO2 scales shall be provided and shall be of the digital readout/electronic load cell type.  Scale frame shall have a 2-part epoxy finish and be sized to accept _____ (1 or 2) 3,600 lb (1632/kg) container(s).  The frame shall have the required number of heavy duty bronze bushed bearing trunnions installed for each container to allow easy container rotation.    Scale shall be of such a size that it is within the dimensions of the tank(s) it supports.

Scale shall be of the single load cell design.   Weight shall be transferred via levers to a single, NTEP approved load cell of the shear beam strain gauge type.  Flexible cable shall connect load cell to indicator to allow easy remote installation of the readout.  Cable length shall be _____ (20'/6M standard).

Indicator shall monitor__________(1 or 2 ) channels. The remote mounted LCD indicator shall carry CE marking and shall be housed in a NEMA 4X, UL approved enclosure. All operations shall be keypad operated & menu driven in order to avoid compromising the NEMA 4X seal at anytime.  The alphanumeric LCD readout shall have backlighting for readability in low light conditions.  Power requirement shall be ______________( 110 VAC, 220 VAC or 24 VDC)

A 6 digit numerical display shall give operator the ability to monitor chemical by weight (lb or kg) or volume (gallons or liters).  A bar graph display shall read 0-100% for the net contents.  A dual mode TARE key shall allow user to enter the tare weight of the vessel or enter the net weight of the chemical depending on application needs. A diagnostics menu shall allow recalibration without the need to apply field test weights.  A user adjustable filter function shall stabilize display in the event of vibration from pumps or mixers in the immediate vicinity of the scale.

Indicator shall output net weight via a 4-20mA signal and full scale output shall be user adjustable via the keypad.  Indicator shall have four adjustable set points to display low or high level conditions on the indicator.

OPTIONAL:    Set points shall activate ______ (up to four) ½ Amp dry contact relays.

Scale shall carry a Full Five (5) Year Factory Warranty.  “Limited” Warranties shall be considered unacceptable.    Full scale accuracy shall be better than 1/4 of 1%.    Scale shall be CHLOR-SCALE® Model DR_____, and electronic SOLO® G2 digital indicator Model SRG2-____ (1 or 2 channel), as manufactured by FORCE FLOW, 2430 Stanwell Drive, Concord, CA  94520 USA (www.forceflow.com).

Model Numbers:

INDICATOR:	SRG2-1		One Channel

SRG2-2 		Two Channel

PLATFORM:

No. of Ton Containers	Model No.  (Capacity lbs)	Metric Model (Capacity kgs)

1-Tank Scale		DR40	(4000 lb.)		DR20K	 (2000 kg.)

2-Tank Scale		DR80	(8000 lb.)		DR40K	 (4000 kg.)

FORCE FLOW   1-800-893-6723

FAX: 925-686-6713    www.forceflow.com    info@forceflow.com

TON/SOLO G2

02/26/09