TYPICAL SPECIFICATION

WIZARD® 4000

SINGLE or DUAL TANK TON CONTAINER SCALE

SPECIFICATION  SECTION 11261 - Chlorination Equipment:

SCALE PLATFORM:    A quantity of ______ Chlorine/SO2 scales shall be provided and shall be of the digital readout/electronic load cell type.  Scale frame shall have a 2-part epoxy finish and be sized to accept _____(1 or 2) 3,600 lb/1632 kg. chlorine or sulfur dioxide container(s).  The frame shall have the required number of heavy duty bronze bushed bearing trunnions installed for each container to allow easy container rotation.    Scale shall be of such a size that it is within the dimensions of the tank(s) it supports.  Scale shall be of the single load cell design.  Weight shall be transferred via lever(s) to a single, NTEP approved, load cell of the shear beam strain gauge type.  Flexible cable shall connect load cell to indicator to allow easy remote installation of the readout.  Cable length shall be _____ ft. (meters) (20'/6M standard).

INSTRUMENT ENCLOSURE, OUTPUTS & ALARMS:  Indicator shall carry CE marking and shall be housed in a NEMA 4X, UL approved enclosure.   Indicator shall have a 20 key digital keypad & ability to display 2 scales at a time on a backlit alphanumeric display.  If more than 2 scales are being monitored, display shall automatically scan all scales in the system.   Indicator shall have adjustable 4-20mA signals that output net weight and chemical feed rate for each scale.  Indicator shall display an alarm in any of the following conditions: Low level, high level, low feed rate, high feed rate, max daily use, min daily use, supply exhausted and load cell failure.  An alarm log shall store the most recent 10 alarm conditions with time and date of occurrence.  A quantity of ____ relays (up to 12 per indicator) shall be provided for remote alarm indication or transfer pump control.   Indicator shall be enabled with MODBUS protocol for remote RS-485 serial communications.

DISPLAY & INVENTORY CONTROL SOFTWARE:  Keypad and Menu items shall have independent password protection to prevent unauthorized operation.  Both a numerical and a bar graph display shall give operator the ability to monitor chemical by weight, volume or percent full.    Each channel shall have a user selectable, two digit scale ID number and shall display net remaining, pure chemical remaining, feed rate, daily usage, total amount used, days until empty, gross weight and tare weight.    A TANK LOAD key shall pause & project usage accumulation during chemical re-supply to maintain accurate usage data over multiple tank loads.  A data log shall store the DAILY USAGE for each of the previous 31 days.  Indicator re-calibration in the field shall be accomplished through the keypad and shall not require the use of dead weights.

Scale shall carry a Full Five (5) Year Factory Warranty.  “Limited” warranties shall be considered unacceptable.   Full scale accuracy shall be better than 1/4 of 1%.   Scale shall be CHLOR-SCALE® Model DR______ and WIZARD 4000® digital display Model 4000-___, as manufactured by FORCE FLOW, 2430 Stanwell Drive, Concord, CA 94520 USA (www.forceflow.com).

Model Numbers:

PLATFORM:

No. of Ton Containers	Model No. (Capacity lbs)	Metric Model (Capacity kgs.)

1-Tank Scale		DR40   (4,000 lbs)		DR20K   (2,000 kgs)

2-Tank Scale		DR80   (8,000 lbs)		DR40K   (4,000 kgs)

NOTE:   2- tank scale is designed for systems that have 2 tanks manifolded, feeding simultaneously.

INDICATOR:			4000-1	 One Channel

4000-2    Two Channel

4000-3    Three Channel

4000-4    Four Channel

File: _WEB\SPECS\SPCTONWZ

FORCE FLOW 1-800-893-6723

FAX: 925-686-6713

TON/WIZ

09/03/03