TYPICAL SPECIFICATION

WIZARD® 4000

VOLUMETRIC FEEDER SCALES

SPECIFICATION SECTION 11245 - Chemical Feeders

SPECIFICATION SECTION 11240 - Chemical Metering Pumps

A quantity of ____volumetric feeder scales of __________ lbs. (kgs.) capacity shall be provided and shall be of the digital readout/electronic load cell type.  Scale platform shall have feeder mounting holes pre-drilled in the platform for ease of installation and to secure the feeder to the scale.   Platform scale coating system shall be a minimum dry thickness of 80 mils and be resistant to moisture, chemicals, abrasion, impact and UV light.

Scale shall be of the three load cell design.  All load cells shall be NTEP approved, and of the shear beam strain gauge type.  Flexible cable shall connect load cell to indicator to allow easy remote installation of the readout.  Cable length shall be _____ ft. (meters) (20'/6M standard).

INSTRUMENT ENCLOSURE, OUTPUTS & ALARMS:  Indicator shall carry CE marking and shall be housed in a NEMA 4X, UL approved enclosure.   Indicator shall have a 20 key digital keypad & ability to display 2 scales at a time on a backlit alphanumeric display.  If more than 2 scales are being monitored, display shall automatically scan all scales in the system.   Indicator shall have adjustable 4-20mA signals that output net weight and chemical feed rate for each scale.  Indicator shall display an alarm in any of the following conditions: Low level, high level, low feed rate, high feed rate, max daily use, min daily use, supply exhausted and load cell failure.  An alarm log shall store the most recent 10 alarm conditions with time and date of occurrence.  A quantity of ____ relays (up to 12 per indicator) shall be provided for remote alarm indication or transfer pump control.

DISPLAY & INVENTORY CONTROL SOFTWARE: Keypad and Menu items shall have independent password protection to prevent unauthorized operation.  Both a numerical and a bar graph display shall give operator the ability to monitor chemical by weight, volume or percent full.    Each channel shall have a user selectable, two digit scale ID number and shall display net remaining, pure chemical remaining, feed rate, daily usage, total amount used, days until empty, gross weight and tare weight.    A TANK LOAD key shall pause & project usage accumulation during chemical re-supply to maintain accurate usage data over multiple tank loads.  A data log shall store the DAILY USAGE for each of the previous 31 days.  Indicator re-calibration in the field shall be accomplished through the keypad and shall not require the use of dead weights.

Scale shall carry a Full Five (5) Year Factory Warranty.   “Limited” warranties shall be considered unacceptable.   Full scale accuracy shall be better than 1/4 of 1%.   Scale shall be VOLUMETRIC FEEDER SCALETM , with TUF-COATTM Environmental Armor, Model ___-DR____VF__ ,  and WIZARD® 4000 digital display Model 4000-__ ,  as manufactured by FORCE FLOW,  2430 Stanwell Drive, Concord, CA 94520 USA USA (www.forceflow.com).

Model Numbers:

PLATFORM:			Material		Model No. (Capacity lbs)		Metric Model (Capacity kgs)

Drum-Scale Platform: 	TUF-COAT:	27-DR10VFHA3  (1,000 lbs)		27-DR5KVFHA3 (500 kgs)

(27.5" x 27.5" Platform)	316 SS:		27-DR10VFSHA3  (1,000 lbs)		27-DR5KVFSHA3 (500kgs)

Chem-Scale Platform:	TUF-COAT:	30-DR10VFHA3  (1,000 lbs)		30-DR5KVFHA3 (500 kgs)

(30" x 30" Platform)		TUF-COAT:	30-DR30VFHA3  (3,000 lbs)		30-DR15KVFHA3 (1500 kgs)

316 SS: 		30-DR10VFSHA3  (1,000 lbs)		30-DR5KVFSHA3 (500 kgs)

316 SS:             	30-DR30VFSHA3  (3,000 lbs)		30-DR15KVFSHA3 (1500 kgs)

INDICATOR:			4000-1	One Channel

4000-2	Two Channel

4000-3	Three Channel

4000-4	Four Channel

File: _WEB\SPECS\SPCVFWZ

FORCE FLOW 1-800-893-6723

FAX: 925-686-6713

VF/WIZ

09/03/03